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	REQUEST FOR PROPOSAL (RFP)
For
MDF/IDF Cable Management and Fiber Run Project
Unified School District No. 261, Sedgwick County, Kansas (Haysville)



	PROPOSAL ISSUED DATE:
Wednesday, 
October 7, 2026
	
	PROPOSAL DUE DATE:
Friday,
November 27, 2026
at 11:59 pm CST
	
	PROPOSALS SUBMITTED TO:
https://www.crwconsulting.com/ifcb/ifcb-drfdetail/TkRFeU5UWXg=



Submit RFP questions no later than Wednesday, October 28, 2026, at 11:59 pm CST via the website at: https://www.crwconsulting.com/ifcb/ifcb-drfdetail/TkRFeU5UWXg= 
All bids must be submitted to https://www.crwconsulting.com/ifcb/ifcb-drfdetail/TkRFeU5UWXg= (login as a vendor, choose the district/IFCB you are interested in, then select upload a question or submit a bid)


District Information
Unified School District No. 261, Sedgwick County, Kansas (Haysville) – hereinafter referred to as the District - primarily serves the communities of south Wichita and Haysville. The District has approximately 5200 students and 1100 staff spread across 16 buildings, 14 of which are included in this project.
District Facilities
A complete listing of District facilities to be included in this project can be found in Attachment A.
Project Overview
The District is seeking a vendor to clean up the existing Cat5, Cat6, and fiber cabling in 42 MDF and IDF closets located across 14 buildings. Work will include removing old patch panels and termination points, installing new patch panels, and reterminating existing Cat5, Cat6, and fiber cabling inside closets. The vendor will also install new wall plates and jacks and reterminate the existing cabling at applicable classroom and office locations. All applicable cabling shall be labeled, and cabling terminated or reterminated at both ends shall be tested. Existing switches shall be reconnected to the new patch panels as specified in the Scope of Work. The project also includes replacing existing multimode fiber with single-mode fiber runs as identified in Attachment C.
E-Rate/USAC Funded Project Requirements
E-Rate/USAC funding will be used to help fund this project. The selected vendor must comply with all applicable USAC requirements, including obtaining a Service Provider Identification Number (SPIN). This RFP is limited to E-Rate-eligible equipment and services. Ineligible work shall not be included in proposal pricing. Any award under this RFP is contingent upon E-Rate funding approval and final approval by the USD 261 Board of Education. The District reserves the right to reduce or cancel the project without penalty if E-Rate funding is not approved or is less than anticipated.
E-Rate Consultant Information
The District will be utilizing an E-Rate consultant, CRW Consulting, to assist in the RFP process. All bids and RFP-related questions must be directed to their website, https://www.crwconsulting.com/ifcb/ifcb-drfdetail/TkRFeU5UWXg= .
District Mandatory Tour/Walkthrough
	To participate in the RFP, the proposed vendor must attend a walkthrough of some of the District’s wiring closets on Wednesday, October 21, 2026 at 9:00 am CST or Tuesday, October 27, 2026 at 2:00 pm CST. The walkthrough will be located at The Learning Center, 150 Stewart, Haysville, KS 67060. Bids from vendors that do not attend one of the two mandatory walkthroughs will be disqualified.



Scope of Work
The District is seeking proposals for work in 42 MDF and IDF wiring closets across 14 buildings. For purposes of this RFP, MDF and IDF are collectively referred to as closets, and Cat5, Cat6 and Fiber are collectively referred to as cabling. The specific work required for each closet is identified in Attachment B, which provides approximate quantities and the required scope by closet. The District will provide photographs of the wiring closets to assist vendors with preparing accurate proposals.
Work will include cable cleanup, rack and patch-panel replacement, cable retermination, labeling, testing, switch reconnection, cable management, and fiber optic cable replacement as identified in Attachment C. The vendor shall provide all labor, materials, equipment, testing, documentation, and disposal required to complete the identified work.
The project shall be substantially completed during the District’s summer break. Work may also be scheduled during evenings, nights, or weekends as required. Work shall be performed with no disruption to District network services during normal school and business hours. The vendor shall coordinate the work schedule and sequence of closets with District Technology staff before beginning work. Any required outage must be approved in advance by District Technology staff and performed outside normal operating hours.
1. Photographs and maps: Photographs and maps of all closets & fiber runs will be provided at https://www.crwconsulting.com/ifcb/ifcb-drfdetail/TkRFeU5UWXg=.
1. Cable cleanup and retermination: The vendor shall clean up and organize cabling in each wiring closet and replace racks and patch panels as required. Cat5 and Cat6 cabling included in the work shall be reterminated and labeled at both ends using the T568B wiring standard. At applicable classroom and office locations, the vendor shall replace existing wall plates and jacks with new wall plates and Cat6-rated jacks. Existing fiber cabling included in the work shall also be reterminated and labeled at both ends using LC connectors, except existing multimode fiber being replaced by a new fiber run identified in Attachment C. The only exceptions are individual cables specifically designated by District Technology staff for closet-end work only, which may include access points or other equipment located above ceilings or in difficult-to-access locations. For those cables, the vendor shall reterminate and label only the closet end and leave the equipment-end connection undisturbed. Tracing, reterminating, or labeling the equipment end is not required. Couplers are not allowed unless approved by District Technology. The District can provide a lift if needed. New or replacement Cat5 and Cat6 cable runs are not included in the base scope and shall not be performed without prior written approval from District Technology.
1. Switch placement and patch cables: Relocate switches as necessary to place them directly above or below the associated 24-port patch panels. Use 6” slim 28 AWG Cat6 patch cables where switch and patch-panel placement allow. Reconnect switches using slim 28 AWG Cat6 patch cables rated for PoE Type 4. Use the shortest practical patch-cable length that allows proper routing, bend radius, and serviceability. Patch cable coloring should match color of cable patched down.
1. Connection documentation and reconnection: Certain network connections are assigned to specific switch ports due to VLAN and other network configurations. Before disconnecting any network connection, the vendor shall identify, document, and label the cable, switch, and switch port. This includes connections that do not currently show an active link. After completing the work, return each connection to the same switch and switch port unless otherwise directed by District Technology staff.
1. Cable labeling and documentation: The District will provide the required labeling scheme before work begins. The vendor shall label both ends of all cabling it terminates or reterminates, except cables designated for closet-end work only, which shall be labeled at the closet end only. For closet-end-only cables, the District will provide LLDP documentation for vendor to label cables with. Upon completion, the vendor shall provide the District with an electronic spreadsheet or similar document identifying the building, closet, cable identifier, patch-panel/port, switch/port, and destination when known. Unconfirmed destinations shall be identified as unverified. The vendor shall also provide documentation of all part manufacturers and part numbers.
1. Testing and completion: The vendor shall test all cabling it terminates or reterminates at both ends. Cat5 and Cat6 cabling shall be tested for continuity and correct wiremap on all pairs. Fiber cabling shall be tested for continuity and end-to-end optical loss on all terminated strands. Certification, including OTDR certification, is not required. Vendor testing is not required for cables designated for closet-end work only. The vendor shall provide all required test results to the District. After completing the work and reconnecting equipment in each wiring closet, the vendor shall notify District Technology staff, who will verify network operation. District acceptance of each closet is contingent upon completion of all applicable scope requirements, including cable management, labeling, testing, documentation, rack and patch-panel work, and successful network verification. The vendor shall correct any termination, reconnection, or other deficiencies caused by its work at no additional cost before the District accepts the work in that closet.
1. Workmanship warranty: The vendor shall warrant its workmanship for one year following District acceptance of the applicable work. During this period, the vendor shall correct defects caused by its installation or termination work at no additional cost to the District, including all necessary labor and materials.
1. Fiber runs: Fiber runs & reterminations are identified in Attachment C. All new fiber cabling shall be 12-strand, OS2 single-mode fiber (9/125 µm), with all strands terminated using LC connectors at both ends. Cable shall be plenum rated. Fiber runs shall be continuous end-to-end with no intermediate splices unless specifically approved by District Technology. A minimum 20-foot service loop shall be neatly secured at each end of every new fiber run. The District can provide a lift if needed. Existing multimode fiber being replaced shall be disconnected, neatly coiled, and secured above the ceiling within the applicable wiring closet unless otherwise directed by District Technology.
1. Disposal: The vendor shall place all removed materials in District-provided trash containers at each building.
1. Materials and equipment: All materials and equipment supplied by the vendor shall be new, not used, refurbished, or gray market, and shall meet the District part specifications identified in Attachment E. The proposal must list manufacturer, model or part number, quantity, and unit price.
1. Installation and restoration: All work shall follow manufacturer installation instructions and applicable codes. All wall-mounted racks shall be securely fastened to structural framing, masonry, concrete, or other suitable structural backing using properly sized fasteners rated for the rack and its anticipated load. Drywall anchors alone shall not be permitted. The vendor shall properly seal and firestop all wall, floor, and ceiling penetrations created or disturbed by its work in accordance with applicable codes and the existing fire rating of the assembly. Where an existing telecommunications grounding/bonding system is present in the closet, replacement racks shall be bonded to it. The vendor shall repair any damage to District facilities or existing equipment caused by its work at no additional cost to the District and leave work areas clean and orderly.
1. Third-party equipment and cabling: Existing Zayo, Cox, and other third-party racks, fiber, cabling, and equipment are excluded from this project and shall not be disconnected, modified or reterminated without District approval.
The awarded vendor shall remain fully responsible for completion of all work. Subcontracting is permitted only with prior written approval from the District. The vendor shall identify all proposed subcontractors and the work they will perform and shall ensure that all subcontractors comply with the requirements of this RFP. The services will be awarded to one vendor and will not be separated among multiple vendors. The District reserves the right to determine which buildings to award to stay within the fiscal year budget and may award any, all, or none of the fiber runs and fiber reterminations. Vendors must provide pricing for all 14 buildings to be considered for award. Vendors that do not bid on all locations will be disqualified.
All quantities shown in this RFP are estimates for bidding and E-Rate funding purposes, may change based on actual conditions, and do not represent guaranteed quantities. The District will pay only for the actual quantities of work completed, materials installed, and services performed and accepted by the District, based on the unit prices submitted in the proposal, except that new fiber runs will be paid at the per-run price and fiber reterminations at the per-building price submitted in Attachment D. No payment will be made for estimated quantities not actually provided. Unit prices submitted in the proposal shall remain firm and shall be used to calculate District-approved additions or deductions to the quantities of materials and services included in the original scope. The vendor shall not perform work outside the approved scope or incur additional charges without prior written approval from the District. Pricing must include all hardware, labor, freight, installation, testing, documentation, and disposal. All proposal pricing shall remain firm through contract award and E-Rate funding determination unless otherwise approved in writing by the District.
Proposal Format
Vendors shall upload a PDF copy to CRW Consulting at https://www.crwconsulting.com/ifcb/ifcb-drfdetail/TkRFeU5UWXg= on or before Friday, November 27, 2026 at 11:59 pm PST.
All proposals must include the sections below. Any proposal deemed non-conforming by the Director of Technology and/or Evaluation Committee Chairman regarding format will be considered nonresponsive and will be disqualified.
SUMMARY OF SECTIONS:
A brief explanation of each section is listed below. Vendors shall fully address each section.
1. Pricing for each building, each fiber run, and fiber reterminations by building shall be listed on the pricing worksheet in Attachment D. This worksheet should be located at the front of the proposal and is mandatory.
1. In addition to completing Attachment D, vendors shall provide a separate itemized pricing breakdown identifying each material or service, quantity, unit price, and extended total. Materials and labor shall be identified separately. Unit prices shall include all associated costs applicable to the item.
1. Letter of Introduction – Each proposal must be accompanied by a transmittal letter that must include the following information:
1. Identify the submitting organization.
1. Identify the name, title, telephone number, and email address of the person or persons authorized to contractually bind the organization for this proposal.
1. Be signed by a person authorized to contractually bind the organization.
1. Vendor Profile – Brief history of vendor. Provide information demonstrating the vendor’s background, experience, and ability to complete the required work. Include photographs of at least three separate MDF/IDF closets from similar completed projects that demonstrate the vendor’s cable management, rack installation, patch-panel organization, labeling, and overall workmanship.
1. Timeline – Please describe how this project would be implemented according to the Scope of Work above. This shall include estimated timelines.
1. References – Provide at least 3 references from previous customers (school districts if possible) with similar projects in the past 5 years.
1. Other Value-Added Services or Options – Vendors are encouraged to provide additional information regarding their services or industry knowledge that will support the success of the project. Vendors must provide pricing for the full required scope of work. Any optional alternatives or enhancements must be E-Rate eligible and shall be clearly identified and priced separately from the required work.
1. Provide a sample contract or agreement for the District’s review. Any terms or conditions that conflict with or modify the requirements of this RFP must be clearly identified in the proposal and are subject to District approval.
Insurance Requirements
The awarded vendor shall maintain commercial general liability and workers’ compensation insurance throughout the project and shall provide proof of coverage to the District upon request.
Confidential Material
Any material that is to be considered confidential in nature must be clearly marked as such and will be treated as confidential by the District to the extent allowable by law.
Questions and Answers
All questions regarding the RFP must be directed to CRW Consulting at https://www.crwconsulting.com/ifcb/ifcb-drfdetail/TkRFeU5UWXg= by Wednesday, October 28, 2026 at 11:59 pm CST. Questions limited to walkthrough scheduling may be directed to the District Technology Director. All vendor questions and the District’s answers and RFP updates will be available to all respondents by way of a Q&A page on the District’s consultant website located at https://www.crwconsulting.com/ifcb/ifcb-drfdetail/TkRFeU5UWXg= .
Evaluation Process
A District-appointed Evaluation Committee of at least three (3) members will assess the relative merits of proposals and determine the proposal most advantageous to the District. The price of E-Rate-eligible products and services shall be weighed more heavily than any other single evaluation factor. Proposals may be accepted and evaluated without discussion, and vendors shall not initiate such discussions. If fewer than five proposals are submitted, the Committee may recommend an award or reissue the RFP.
Following evaluation, the Committee will select a finalist, and the Technology Director will notify that vendor. The Committee will recommend for award the vendor whose proposal is determined to be most advantageous to the District. The District will then proceed with contract negotiations. 
The USD 261 Board of Education has final authority in this matter. Any contract resulting from this RFP is subject to final approval by the Board, which reserves the right to reject any or all proposals.
Schedule of Events
	1.
	Wednesday, October 7, 2026:
	This RFP is being issued by the District and will be posted on https://www.crwconsulting.com/ifcb/ifcb-drfdetail/TkRFeU5UWXg= 

	2.
	Wednesday, October 21, 2026 at 9:00 am CST:
	Walkthrough #1 located at The Learning Center at 150 Stewart, Haysville, KS 67060

	3.
	Tuesday, October 27, 2026 at 2:00 pm CST:
	Walkthrough #2 located at The Learning Center at 150 Stewart, Haysville, KS 67060

	4.
	Wednesday, October 28, 2026 at 11:59 pm CST:
	Response deadline to written questions/RFP Amendments. No questions will be answered afterward.

	5.
	Friday, November 27, 2026 at 11:59 pm CST:
	ALL PROPOSALS MUST BE UPLOADED AT https://www.crwconsulting.com/ifcb/ifcb-drfdetail/TkRFeU5UWXg= FOR REVIEW AND EVALUATION BY THE TECHNOLOGY DIRECTOR FOR DISTRIBUTION TO THE EVALUATION COMMITTEE. Proposals received after this deadline will not be accepted.


Thank you for considering this request for proposal. Do not hesitate to contact CRW Consulting at https://www.crwconsulting.com/ifcb/ifcb-drfdetail/TkRFeU5UWXg= if you have questions or need additional information.


ATTACHMENT A – Building Locations
	Building
	Abbreviation
	Address

	Administration Building
	ADM
	1745 W. Grand Ave., Haysville, KS 67060

	Campus High School
	CHS
	2100 W. 55th St. S., Wichita, KS 67217

	Freeman Elementary School
	FES
	7303 S. Meridian, Haysville, KS 67060

	Grand Lane
	GL
	114 Stewart, Haysville, KS 67060

	Haysville High School / Tri-City Day School
	HHS/TCDS
	1975 W. Grand Ave., Haysville, KS 67060

	Haysville Middle School
	HMS
	900 W. Grand Ave., Haysville, KS 67060

	Haysville West Middle School
	HWMS
	1956 W. Grand Ave., Haysville, KS 67060

	Nelson Elementary School
	NES
	245 N. Delos, Haysville, KS 67060

	Oatville Elementary School
	OES
	4335 S. Hoover, Wichita, KS 67215

	Operations Building
	OPS
	1745 W. Grand Ave., Haysville, KS 67060 (driveway next to water tower)

	Prairie Elementary School
	PES
	7101 S. Meridian, Haysville, KS 67060

	Rex Elementary School
	RES
	1100 W. Grand Ave., Haysville, KS 67060

	Ruth Clark Elementary School
	RCES
	1900 W. 55th St. S., Wichita, KS 67217

	The Learning Center
	TLC
	150 Stewart, Haysville, KS 67060




ATTACHMENT B – Cat5/6 Retermination, Patch Panel & Rack Breakdown by Closet
SUMMARY
	Description
	Qty

	24-port modular patch panels
	215

	4u – vertical
	3

	6u – vertical
	2

	12u
	24

	18u
	12

	26u
	4

	42u
	3

	Estimated reterminations in closets
	3,069

	Estimated reterminations in classrooms, offices, etc
	2,075



TERMINATIONS, PATCH PANELS & RACKS NEEDED BREAKDOWN BY MDF/IDF
	Building
	Location
	# on Map
	Closet Reterminations
	Remote End-Reterminations
	24-Port Patch Panel Total
	Rack Model
	Rack Qty

	ADM
	Server Room
	2
	13
	5
	2
	42u
	1

	ADM
	SPED (old IT)
	3
	38
	32
	2
	4u – vertical
	1

	CHS
	Main Office
	1
	99
	68
	7
	42u
	1

	CHS
	F
	2
	169
	153
	10
	18u
	1

	CHS
	E
	3
	48
	25
	4
	12u
	1

	CHS
	D
	4
	107
	86
	7
	18u
	1

	CHS
	B
	5
	58
	47
	3
	12u
	1

	CHS
	A
	6
	130
	113
	8
	18u
	1

	CHS
	I
	7
	51
	32
	4
	12u
	1

	CHS
	Print Shop
	8
	19
	8
	1
	12u
	1

	CHS
	H
	9
	46
	20
	4
	18u
	1

	CHS
	G
	10
	80
	49
	6
	18u
	1

	CHS
	C
	11
	58
	47
	3
	12u
	1

	FES
	Library (C20)
	1
	90
	71
	6
	18u
	1

	FES
	Cafeteria (D11)
	2
	86
	62
	6
	18u
	1

	FES
	B Closet
	3
	38
	27
	2
	12u
	1

	GL
	IT (old HHS)
	1
	91
	83
	6
	12u
	2

	GL
	SBHC Office (old Lab)
	2
	19
	18
	1
	12u
	1

	GL
	PAT (old PS)
	3
	19
	18
	1
	12u
	1

	HMS
	Cafeteria
	1
	33
	15
	3
	18u
	1

	HMS
	C
	2
	141
	115
	9
	18u
	1

	HMS
	B8 (boiler room)
	3
	86
	62
	6
	12u
	2

	HMS
	B
	4
	46
	20
	4
	6u – vertical
	2

	HMS
	H16
	5
	51
	30
	4
	12u
	1

	HMS
	J9
	6
	50
	29
	4
	12u
	1

	HWMS
	Cafeteria
	1
	121
	78
	8
	26u
	1

	HWMS
	Library
	2
	122
	80
	8
	26u
	1

	HHS/TCDS
	Room 187
	1
	137
	92
	9
	26u
	1

	HHS/TCDS
	Room 141
	2
	74
	33
	7
	18u
	1

	NES
	C
	1
	106
	70
	7
	12u
	2

	NES
	A
	2
	123
	87
	8
	18u
	1

	OES
	Stock Room
	1
	116
	62
	8
	18u
	1

	OES
	New Janitor Closet
	2
	36
	26
	3
	4u – vertical
	2

	OPS
	Boiler Room
	1
	31
	18
	3
	12u
	1

	PES
	Office
	1
	109
	21
	9
	26u
	1

	RES
	C
	1
	107
	73
	7
	12u
	2

	RES
	A
	2
	70
	39
	5
	12u
	1

	RCES
	Square
	1
	72
	55
	5
	12u
	1

	RCES
	Triangle
	2
	54
	40
	4
	12u
	1

	RCES
	Circle
	3
	31
	14
	3
	12u
	1

	RCES
	Office
	5
	44
	19
	4
	12u
	1

	TLC
	TLC
	1
	50
	33
	4
	42u
	1

	Totals
	
	
	3,069
	2,075
	215
	
	48




ATTACHMENT C – New Fiber Runs & Reterminations
NEW FIBER RUNS
	Building
	Description
	Closet # From & To
	#/Color on Map
	Est. Feet

	CHS
	A Hall
	6-1
	Brown
	850

	CHS
	B Hall
	5-1
	Purple
	850

	CHS
	C Hall
	11-1
	Blue
	750

	CHS
	D Hall
	4-1
	Green
	600

	CHS
	E Hall
	3-1
	Red
	400

	CHS
	F Hall
	2-1
	Orange
	700

	CHS
	G Hall
	10-1
	White
	600

	CHS
	H Hall
	9-1
	Orange
	450

	CHS
	I Hall
	7-1
	Black
	800

	HMS
	Boiler Room
	3-1
	Brown
	400

	HMS
	B Hall
	4-1
	Orange
	250

	HMS
	C Hall
	2-1
	Purple
	250

	HMS
	H Hall
	5-1
	Green
	300

	HMS
	J Hall
	6-1
	Yellow & Green
	600

	HWMS
	Closet 1 to 2
	1-2
	Red
	550


FIBER RETERMINATIONS
	Building
	Reterminations
	Closet
	Notes

	ADM
	24
	1
	12 SM to Freeman, 12 SM to Operations

	CHS
	12
	10
	12 SM to tennis court

	FES
	12
	1
	12 SM to Admin

	HHS/TCDS
	24
	1
	12 SM to Operations 12 OM3 to Closet 2

	HHS/TCDS
	12
	2
	12 OM3 to Closet 1

	HMS
	24
	1
	12 SM to Rex and 12 OM3 to Ticket Booth

	HMS
	12
	3
	12 SM Boiler to S Gym

	HWMS
	24
	1
	24 SM Concessions and Greenhouse

	NES
	12
	2
	12 SM to Hemphill

	OPS
	24
	1
	24 SM Admin/HHS

	RES
	36
	1
	12 SM to HMS 24 OM3 to Stadium

	
	
	
	

	Totals
	216
	
	




ATTACHMENT D – Pricing Worksheet
Proposal Pricing: Pricing shall be entered into the applicable tables below: (1) Cat5/6 Closet Work Pricing, including parts, labor, and total cost; (2) New Fiber Runs Pricing, priced per run; and (3) Fiber Reterminations Pricing, priced by building. Lump-sum pricing without this detail will not be accepted. This worksheet should be located at the front of the proposal. Yellow shaded cells are to be completed by the vendor.
	Scope
	Total Cost

	Cat5/6 Closet Work
	

	New Fiber Runs
	

	Fiber Reterminations
	

	TOTAL PROPOSAL COST (all closet work, fiber runs & fiber reterminations)
	



CAT5/6 CLOSET WORK PRICING
	Building
	Parts
	Labor
	Total

	Administration Building
	
	
	

	Campus High School
	
	
	

	Freeman Elementary School
	
	
	

	Grand Lane
	
	
	

	Haysville High School / Tri-City Day School
	
	
	

	Haysville Middle School
	
	
	

	Haysville West Middle School
	
	
	

	Nelson Elementary School
	
	
	

	Oatville Elementary School
	
	
	

	Operations Building
	
	
	

	Prairie Elementary School
	
	
	

	Rex Elementary School
	
	
	

	Ruth Clark Elementary School
	
	
	

	The Learning Center
	
	
	

	Optional – Vendor’s discount if the district decides to award the contract for all listed locations.
	
	
	

	TOTAL BUILDING/CLOSET WORK
	
	
	



NEW FIBER RUNS PRICING
	Building
	Description
	Closet # From & To
	Est. Feet
	Total Cost

	Campus High School
	A Hall
	6-1
	850
	

	Campus High School
	B Hall
	5-1
	850
	

	Campus High School
	C Hall
	11-1
	750
	

	Campus High School
	D Hall
	4-1
	600
	

	Campus High School
	E Hall
	3-1
	400
	

	Campus High School
	F Hall
	2-1
	700
	

	Campus High School
	G Hall
	10-1
	600
	

	Campus High School
	H Hall
	9-1
	450
	

	Campus High School
	I Hall
	7-1
	800
	

	Haysville Middle School
	Boiler Room
	3-1
	400
	

	Haysville Middle School
	B Hall
	4-1
	250
	

	Haysville Middle School
	C Hall
	2-1
	250
	

	Haysville Middle School
	H Hall
	5-1
	300
	

	Haysville Middle School
	J Hall
	6-1
	600
	

	Haysville West Middle School
	Closet 1 to 2
	1-2
	550
	

	
	
	
	
	

	TOTAL COST FOR NEW FIBER RUNS
	8,350
	




FIBER RETERMINATIONS PRICING
	Building
	Reterminations
	Total Cost

	Administration Building
	24
	

	Campus High School
	12
	

	Freeman Elementary School
	12
	

	Haysville High School / Tri-City Day School
	36
	

	Haysville Middle School
	36
	

	Haysville West Middle School
	24
	

	Nelson Elementary School
	12
	

	Operations Building
	24
	

	Rex Elementary School
	36
	

	
	
	

	TOTAL COST FOR FIBER RETERMINATIONS
	216
	




ATTACHMENT E – District Part Specifications
	Item
	Description

	Rack – Wall Mount
	24” depth (when possible), not enclosed, square hole, Rackstuds preferred

	Rack – Floor Mount
	4 post, 43” depth

	Patch Panel – Cat5/6
	Modular, 24-port, Keystone compatible, no coupler style

	Patch Cable – Cat5/6
	Slim 28 AWG Cat6 patch cables rated for PoE Type 4

	Patch Panel – Fiber
	All LC

	Patch Cable – Fiber
	Single Mode

	Single Mode Fiber Cable
	12-strand, OS2 single-mode fiber (9/125 µm)

	Wall Plate Jacks
	Keystone compatible

	Wall Plates
	Keystone compatible
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